## Sheet1
Technical Questionnaire - 26CH1B-CHI-1001&1002&1003 Chillers
| Question | Supplier reply
Package Duty and Regulation
1 | Nominal cooling power required for the package is 2500 kW (~835kW per unit). Regulation range is 0-100% to be achieved without continuous start/stop of machines. Please identify the different regulation methods that will be applied in required regulation range.
2 | Target Temperature at the mixing point downstream the three Unit Evaporators is 6°C. Water flow is constant and equally distributed to the 3 units. Vendor to clarify if target temperature can be achieved in all operating cases as per Appendix C of the technical summary. If strictly required during transients or unfavourable operating conditions, slight deviations to the target temperature can be accepted.
3 | Refrigeration package shall be available to operate in all environmental conditions included in section 4.2 of Technical Summary. i. No glycol will be used in the chilled water circuit. Please confirm that all required anti-freezing protection will be included in the scope (e.g. for evaporator and chilled water piping in the scope of vendor, for air cooled condensers during extreme winter conditions). ii. Is this protection effective even there is no flow on chilled water circuit?
4 | Can Vendor Guarantee the availability requirement included in section 4.1 of the Technical Summary? Can a RAM (Reliability, Availability and Maintainability) study be performed by Vendor if required?
Qualification
5 | Package is classified as Safety Important Class SIC-2. Package instrumentation and control components that fulfil safety functions are SIC-2B classified. Has Vendor already provided chiller units that have been fully qualified for Nuclear Applications?
6 | Can vendor Provide RCC-E category K3 qualified Electrical and Instrumentation equipment
7 | Do Vendor propose a PLC fully qualified for Nuclear Applications (including Software/Algorithms)? If a fully qualified complete PLC is not available, can Vendor propose a parallel (hardwired) Safety Control System to take care of the basic safety function when main control system is not available?
8 | Is vendor able to provide qualification to static magnetic fields as per section 4.2 of Technical Summary?
9 | Units have to guarantee full functionality during and after a SL-2 Seismic Event. i. Can proposed chillers be qualified to the seismic load included in Appendix D of Technical Summary? ii. Is this achieved with or without Seismic Isolation Devices? iii. Has supplier already performed or is able to perform a shaking table test on complete units.
10 | Is Vendor able to demonstrate that proposed equipment can fulfil its safety functions during all required operating life (30 years)?
Materials of Construction
11 | Stainless Steel has been required as base case material for parts of the chillers in contact with chilled water (e.g. evaporator tubes and water boxes). Please confirm supply of stainless steel or indicate alternative proposed material suitable for chilled water parameters included in section 4.1 of the technical summary (e.g. pH range = 6.5-7.5 ).
12 | Vendor to confirm that materials exposed to the outdoor environment (e.g. air cooled condensers) shall withstand ambient conditions included in section 4.2 of the technical summary.
Installation
13 | Installation Area is Outdoor (unsheltered). A container/cabinet is required to protect from extreme environmental conditions all components in the scope except forced air condenser that will be installed on the roof of the container itself. Is supplier able to supply this kind of configuration fulfilling all other requirements included in the Technical Summary?
14 | Installation layout is included in appendix E of Technical Summary. Foundation Plinths with their embedded plates have already grouted. Supplier to confirm that available footprint for each unit is (~9150x2440 mm) and distance between adjacent chillers (~2050mm) can be respected